PROCEDURES FOR THE EXAMINATION OF PLANS AND INSPECTION OF CONSTRUCTION

Contents

INTRODUCTION

- EXAMINATION OF PLANS

1.1	Function of the Building Inspectorate

1.2	Building Inspector

1.3	Development Control Officer (Engineer)

2.	INSPECTION OF CONSTRUCTION

2.1	General

2.2	Building layout

2.3	Foundations

2.4	Structural Frame

2.5	Ring Beam

2.6	Roof

2.7	Floors

2.8	Plumbing

2.9	Drainage

2.10	Septic Tank and Waste Disposal

2.11	Water Cistern

2.12	Electricity

2.13	Final Inspection

2.14	Special Inspections

2.15	Other Inspections

2.16	Safety and Health Inspections

3.	COMPLEX OR LARGE PROJECTS

4.	BUILDING ADVISORY SERVICE FOR SMALL BUILDINGS

5.	REPORTING

Appendices

Forms

1A.	Review of Plans of Small Domestic Buildings

1B.	Results of Examination of Plans

2.	Request for Inspection

3	Building Inspection Report

4.	Monthly Report

5.	Design Requirements for Consideration by Building Consultants

6.	Certificate of Practising Structural Engineer

INTRODUCTION

This document is based on discussions and observations of the procedures used by most of the OECS building inspectorates for the examination of plans and the inspection of construction. The problems noted are that generally not enough time is taken for the examination of the plans and the details on the drawings observed by the Building Inspectors are not generally in accordance with the requirements of the Guidelines.

The document does not discuss the procedures for receipt of the applications, as each Authority will have its own procedures. However, the examination of plans and the reporting of the examinations must be carried out in an orderly manner, and attention is therefore given to the procedures for doing this.

The use of the Building Guidelines and Building Code for buildings to be erected in Antigua and Barbuda and in St. Kitts and Nevis is now the law of the land. The Code defines small buildings as those residential and retail commercial buildings less than 3000 sq. ft. in area, and therefore covers most (in numbers) of the buildings being constructed in the State. The requirements of the Code control the design and construction of all buildings; but the Guidelines are geared for use by the designer and constructor of small buildings.

The Building Inspectors have to ensure that all developments are carried out in accordance with the Code and with the relevant plans as approved by the DCA. The procedures outlined are intended to guide the building inspectorate in carrying out the required inspections, but each Inspector must be knowledgeable about the existing building and planning Regulations and must be aware of the main recommendations detailed in the Code and Guidelines.

The Sections on the Administration of the Code and on the Administration of the Guidelines  define the inspections which are mandatory. Site Inspection visits are based on requests by the developer or builder on the forms as at Appendix 1.

The visits paid to construction sites by the Building Inspectors must be formal and within normal working hours unless specifically requested by the builder to carry out an inspection after working hours for a specific purpose, such as during a concrete pour.

There is also the need for the Building Inspectors to assist builders of small homes in the construction techniques needed to permit "safe' construction, and it is recommended that an Advisory Service be established to provide this assistance.

Many persons building small homes do not have the knowledge needed to design and construct a safe and economical home. It is proposed that the Building Inspector accept the challenges of assisting the homeowner by explaining the requirements of the Building Guidelines and the process required by the Authority for applying for a development permission and for a permit to construct the home. It is not intended that the Building Inspector design the home but he/she should discuss the construction details with the home owner or builder. The details given in the Guidelines and for timber homes in the document “Build it Strong” should be followed by the home owner.

The Advisory Service if established can be an important function of the DCA. The procedures for this service are outlined in Section 4.

Unless the regulatory body is equipped with personnel capable of carrying out the examinations of major structural or infrastructure works, it is assumed that the building inspectors concentrate on the examination of plans for buildings within the scope of the Building Guidelines. Plans for major works outside the scope of the Guidelines should be examined by professional engineers and architects employed by the Public Works Department.

1.	EXAMINATION OF PLANS

1.1	Function of the Building Inspectorate

The examination of plans is part of the procedures for processing of applications; however, the involvement of the building inspectorate at this stage will assist the Development Control Officer and the Director (Town and Country Planner) in determining the need for other opinions on the proposals and for discussions with developers.

The examination should be carried out systematically and in accordance with the details given in the Building Code and Guidelines. All construction details must be as per the Code and Guidelines and must satisfy the requirements of the Code; or the designer will be expected to provide calculations or other information showing that the details shown on the drawings would produce a hurricane and earthquake resistant building and that the facilities being constructed are in accordance with the Code.

The Code recognises that there are occasions in which a Special Inspector may be required to assist the DCA in the examination of plans and construction of specialized installations. The Development Control Officer is expected to advise the Director  whether a Special Inspector is required giving reasons for this advice. The reasons must be in accordance with Section 1of the Code.

Until the Dept. of Planning engages a plumbing specialist, the Senior Building Inspector should examine all plumbing layouts using the Building Guidelines for guidance. The examination should focus on:

-	the adequacy of pipe sizes and connections;

-	ensuring that there is no possibility of cross connection between the potable water lines and waste lines;

-	the design and placement of septic tanks, cess pits and disposal wells should be examined. If plans for these facilities are not available, the designer should be asked to submit them for consideration before the application is forwarded to the DCA. The Ministry of Health should be consulted at an early  stage for advice on all plans for disposal of waste.

1.2	Building Inspector

a)	The Building Inspector will be expected to examine the plans for the following:

b)	Type of building (see regulations) and of structural frame

c)	Design of foundations

d)	Hurricane holding down bolts and clips

e)	Size of structural members

f)	Roof structure, pitch, sheathing and fixings

g)	Concrete block wall sizes and reinforcing

h)	Ring beam size and reinforcing

i)	Water cistern size and construction details

j)	Septic tank size and construction details

k)	Disposal of storm drainage. The drawings must show the guttering and the path of the run-off of the water, whether into a cistern or into a road drain.

l)	Plumbing arrangements ( in concert with the Senior Building Inspector) and pipe sizes for internal connections and  arrangements for connections to the main water supply system and to the mains sewer system where applicable.

m)	Electricity (with the Electrical Inspector)

n)	The Building Inspector reports on the examination using the form at Appendix ----- and then passes the file to the Development Control Officer for his further action.

1.3	Development Control Officer (Engineer)

The Development Control Officer carries out the following:

a)	Determines whether a Special Inspector should be recommended for the review of the structural plans or other plans as required in Section 1 of the Code, and to assist in the inspection of construction of the structure and of any other specific component of the development beyond the scope of the Guidelines.

  - Examines the plans to determine whether the structural designs shown are in accordance with the Code. The Development Control Officer may request the applicant to supply structural calculations if this is considered necessary. If there no engineer in place, the Public Works Department should be asked to review the drawings for compliance with  the Code, or a Special Inspector may be engaged to carry out this work.

c)	Reviews all comments on the file received from the Senior Building inspector and from the Departments/Authorities consulted and prepares the recommendation to the DCA for the consideration of the Director. The file is then passed to the Director for his action.

d)	The examination of the plans is complete only after the Development Control Officer is satisfied that the plans submitted are responsive to the Building Code and/or Guidelines, and that the information given is adequate for such a determination.

e)	The Development Control Officer may recommend to he Director that the application be approved or not approved based on the examination of the plans and the comments received.

2.	 INSPECTION OF CONSTRUCTION

2.1	General

a)	Inspection of construction follows the approval of the application and the request of the builder. Each sheet of plans and specifications approved by the DCA must be stamped and dated as approved and signed by the Secretary.

b)	The Code and Guidelines give the stages at which the Inspectors are expected to examine the work and to approve or otherwise the work examined so that the builder can move on to the following phase.  The following should be examined:

2.2	Building Layout.

The actual layout of the buildings or developments should be checked against the approved plans. The Building Inspector should ask the person in charge of the site to produce a copy of the approved plans, before beginning the check. While the site boundaries may be difficult to check by the Building Inspector, the site boundaries should be marked and the Building Inspector should satisfy himself that the construction is within the required distances from the site boundaries and is in accordance with the approved plans.

2.3	Foundations.

a)	Many building plans are submitted without a precise knowledge of the soil types or without the topography shown. During construction the builder finds that the level of the land is such that a level footing is not practicable and decisions have to be made on the depth of the footing below ground level and the size of the footing.

b)	In such circumstances the Building Inspector has to decide whether the amendments made on site are satisfactory or whether the developer should apply to the DCA for approval of the amendments found necessary by site conditions. On a large project advice on such problems would be given by the Special Inspector, (where employed) but on small projects it is expected that the Building Inspector would examine the suggested variation to the plans and advise the builder whether work can continue without requiring the approval of the DCA.

c)	The following procedure should be used:

i)	For large projects, request the developers or builders to provide soil tests and foundation designs based on the ground profile and strata (and other relevant data) on which the footing is to be placed.

ii) 	Inspect the foundations before concreting takes place to check whether the footings are being constructed as designed. If this is not being done, the builder or developer should be requested to provide amended drawings for consideration of the DCA. For large projects the builder should be advised to cease work until the DCA has approved the amendments.

iii)	For small projects, check to see whether the footings are being constructed as per the Guidelines, and that the base of the footing if on rock, is keyed into the base material as given in the Guidelines. It is important to ensure that the footings can not be eroded by storm water or if near the sea, by high seas or storm surge affects.

2.4	Structural Frame.

a)	Where the structural frame is of timber, the Building Inspector should check the connectors used to ensure that they are adequate for the size of timber being used, and that the connectors are properly placed. If the frame is a concrete block wall the size and reinforcing of the walls and ring beam must be in accordance with the approved drawings and with the Guidelines..

b)	Concrete quality if mixed on site. Concrete tests should be carried out to assist the builder to produce concrete of the strength required by the Guidelines.

2.5	Ring Beam

The Building Inspector should check to see that the size being used is as per the approved plans and in accordance with the recommendations of the Guidelines and that the reinforcement is adequate. The quality of the concrete should also be examined. Badly constructed formwork produces generally bad quality concrete. It is expected that the Building Inspector will guide the small builder in the construction of adequate formwork for ring beams and lintels.

2.6	Roof.

a)	The Building Inspector will be expected to ensure that the roof structure is constructed as designed, and in particular to see that the roof plates are properly bolted to the ring beam and that the rafters are connected to the plate by bolts or acceptable connectors. Reinforcing rods bent around the rafters is not the preferred method.

b)	The roof sheeting should be connected to the rafters and purlins by screws rather than nails, as screws provide better resistance to high winds. The roof sheeting itself should be supported at intervals as shown in the Guidelines so that there is no sagging. Where corrugated galvanised iron sheets are used gauge should preferably 24 rather than 26 in common use.

2.7	Floors

a)	Timber floors shall be constructed as per the Guidelines. Examine the sizes and placing of floor joists and fixing of joists to main beams or to wall plates.

b)	For concrete floors ensure that the fill is properly placed to prevent subsidence, and that the concrete is vibrated or properly tamped to provide dense concrete. A proper screed well floated will prevent dusting during use and provide a surface that will wear well.

c)	Check the reinforcement to see whether it conforms to the plans and to the Guidelines

2.8	Plumbing

a)	The Building Inspector must ensure that the workmanship is sound and that the layout of the system is as per the design examined and approved by the DCA.

b)	The Building Inspector must check to see that there are no cross connections between the water lines and the waste lines, and that there is no possibility of contamination of drinking supplies by waste water.

c)	The Guidelines give appropriate gradients for pipes of the sizes recommended. The sizes  should be checked on site as the drawings for small buildings might not show the pipe sizes or the gradients to be used. Also all waste pipes must be trapped and vented in accordance with the Guidelines. These must be checked.

2.9	Storm Water Drainage

The Building Inspector should check to ensure that the guttering supplied is properly connected and that all roof water is led to the cistern or to a road drain as shown on the drawings.

2.10	Septic Tank and Disposal System

The construction of the tank must be carefully monitored, The drawings approved by the DCA must be followed. It would be useful to have some of the inspections of the tank and disposal system done by the Ministry of Heath.

2.11	Water Cistern

a)	The requirement for the construction of water cisterns is necessary due to the low rainfall in the some situations in Antigua and Barbuda. The Guidelines require that for standard dwelling houses not connected to a mains supply, the size of the cistern be calculated on the basis of 10 gallons per sq. ft. of roof area. The Building Inspector must check that this requirement is being met.

b)	The construction details of the cistern should be shown on the drawings. In general the deeper the cistern the thicker should be the cistern walls. The Building Inspector should check the construction as per the drawings and ensure the proper placing of reinforcement. Each cistern must have an access hatch and should preferably be constructed with two chambers so as to allow for cleaning of the cistern without having to dispose of all of the water.

c)	Be sure that soil or waste pipes are not routed through the cistern, or that the cistern is not built under a garage where leaking oil can get into the water.

2.12	Electricity

Inspections should be done in concert with the Electrical Inspector. The inspections should begin with the placing of conduits (where required) and at the stage when the conductors are being pulled. The Electrical Inspector will determine the stages of inspection and the Building Inspector will be expected to inform the Electrical Inspector of the progress of the construction and cooperate in the inspection.

2.13	Final Inspection

The permission to occupy a newly constructed building is dependent on the issuance of a Certificate of Occupancy. This certificate can only be issued if the final inspection has taken place and the Building Inspector is satisfied that the building has been constructed in accordance with the approved plans.

The Building Inspector should therefore carry out this inspection with the builder present. The inspection should include all major systems, such as sewage disposal, electricity, water cistern, drainage, and final covering of roof. The inspection will take at least three hours for a building of 3000 sq.ft. and should not be hurried.

2.14	Certificate of Occupancy

This certificate should be provided the day after the final inspection if the inspection shows that the building construction is satisfactory. If problems are noticed, the builder and developer must be informed and another inspection planned. Information to the builder and developer must be confirmed in writing addressed to the developer or his/her agent as given in the application form.

2.15	Other Inspections

The Special Inspector should be engaged for examination of major  mechanical and electrical systems such as desalination plants, mechanical sewerage treatment plants, and power plants. Reports of the Special Inspector will be sent to the Director and copies sent to the builder and developer for action where indicated. Inspections of major civil engineering works also fall in this category, and should be handled similarly.

2.16	Safety and Health

a)	Section 6 of the Code details the requirements for safety precautions during construction. This requirement applies to all work whether on small or on large projects. The Building Inspector must be aware of the requirements of this Section of the Code, and ensure that builders comply with the provisions where applicable.

b)	In particular all mechanical hoisting equipment must be examined to ensure that the equipment can be operated safely.

c)	During periods of hurricane watch the builder should secure all material that can be moved by high winds, and all loose material must be removed. In order to ensure that the requirements of the Code are observed the Development Control Officer should notify all building sites to secure the premises and material as soon as the hurricane watch is announced. This can be done through the National Disaster Coordinator in the warning messages given on the radio.

d)	Section 5 of the Code gives the minimum standards required for public health and safety. Most of the requirements can be examined during the stage of processing of applications, but requirements for sanitation on building sites and general cleanliness of the site must be enforced by the Building Inspector. There should be no exceptions to this requirement, and the diligence of the Building Inspector is important in ensuring that a tidy building site is maintained. The Central Board of health should be informed if in the opinion of the Building Inspector the construction site is not being maintained in a safe and healthy manner.

3.	COMPLEX OR LARGE PROJECTS

3.1	The Code (Section 1) details the requirements for the Special Inspector(or Review Consultant) and gives the responsibilities of the  position. The Special Inspector reports to the Director (through the Development Control Officer). The reports must be submitted monthly and as needed by the progress of construction. The terms of reference of the appointment must therefore include this specific requirement, the details of which should be developed during negotiations with the developer, and submitted to the DCA with the comments made on the application.

3.2	The Special Inspector must have the following qualifications:

a)	Recognised qualifications as an Engineer or Architect

b)	Proven experience in the design or construction of projects similar to the project being examined

c)	Experience as a resident engineer or architect on major projects, or specific experience in the installation of major mechanical, electrical or electronic equipment as may be deemed necessary.

3.3	It must not be assumed that a Resident Engineer or Clerk of Works employed by the developer can perform the duties of the Special Inspector. This determination must be made by the Director who will take into account the qualifications and experience of the engineer, the nature of the tasks to be performed and the special reporting function of the Special Inspector.

3.4	The reports of the Special Inspector will determine whether the Development Control Officer is satisfied that the project concerned has been constructed in accordance with the Code and other requirements and can on completion of the project recommend the issue a Completion Certificate.

3.5	It is important therefore that the Building Inspector ensure that the reports of the Special Inspector are clear and unequivocal in its conclusions so that the Director can issue the Completion Certificate with confidence.

3.6	Appendix 5 provides forms to be filled out and submitted by the Prime Consultant and Structural Engineer engaged for projects beyond the scope of the Guidelines. The proper use of these forms will provide some comfort to the Authority that the Consultants have examined and taken into account the design requirements for buildings to resist the natural hazards of high winds, heavy rainfall and earthquakes. These forms must accompany the submissions for building permits for buildings within the Groups indicated on the forms. The Director will not examine any submission that is out accompanied by the forms properly filled out.  The Senior Building Inspector on receipt of the applications for building permits must ensure that the forms have been attached to the applications and that the critical criteria have been considered by the Consultants.

4.	BUILDING ADVISORY SERVICE FOR SMALL PROJECTS

4.1	Advice offered to small builders at the planning and designing stages would prevent many problems in the building process. Persons wishing to design and construct small buildings should request advice from the Department when the buildings are being planned.

4.2	The procedure to be used in providing the advice is as follows:

a)	The service would normally begin with the application for development permission and a review of the plans. The Senior Building Inspector should arrange a meeting with the developer or builder to discuss all details which would lead to the production of safe and economical construction. It is not intended that the Advisory Service deal with the planning aspects of buildings except in areas where the Code requires specific planning requirements, such as size and location of bathrooms.

b)	Assistance is given in areas such as:

-	Filling out the application form

-	Explaining the Guidelines

-	Foundation design

- 	Reinforcement of columns and beams

-	Design of septic tank and soakaway pit

-	Design of water cistern

-	Roof design and holding down mechanisms

-	Other matters which may be of concern to the builder.

4.3	The Senior Building Inspector should inform the builder that the advice offered is intended to produce buildings which would conform to the requirements of the Guidelines and the Code. The responsibility for the design and construction of the building remains with the developer or builder and not with the Authority/Board.

4.4	The builder should be advised to discuss the electrical installations with the Electrical Inspector at an early stage, so that provision can be made for installation of conduits (where needed) and the circuit breaker.

5.	REPORTING

5.1	Appendices 1, 3 and 4 give the reporting forms to be used by the Building Inspectors. The general procedure for ensuring consistent reporting records is as follows:

a)	All reports must be placed on the relevant file.

b)	Reports must be identified by the plot and parcel number and the Permission Certificate number.

c)	Drawings must be folded in envelopes and stapled to the file. Large developments will produce many drawings which cannot be placed in envelopes. In such circumstances the package or roll must be properly tagged with the application number and filed. The location of these drawings should be noted on the file.

d)	Reports should be made on each project under construction at intervals no greater than two months, and on the result of every inspection. Reports must indicate clearly action to be taken by the Director or Engineer or other officers of the DCA.

e)	All reports are received by the Senior Building Inspector and each report filed appropriately. The computer record is updated at that time.

f)	The files must be passed to the Engineer no later than noon of the day the reports are received, so that the Engineer can examine the reports and take appropriate action.

g)	Copies of all letters sent by the Director on matters arising from the reports should be sent to the Engineer who should ensure that the Building Inspector who generated the report is informed of the action taken.

f)	The Review Committee should examine the reports and to ensure that appropriate action is taken where indicated.

h)	Each report should be subjected to a searching analysis, as many major problems do not necessarily surface on the reports.

i)	The monthly DCA reports should be examined by the Director before being submitted to the DCA, and forwarded to DCA with comments by the Director. All problems noted and action taken should be reported to the DCA.

APPENDIX 1A

REVIEW OF PLANS OF SMALL DOMESTIC BUILDINGS

(Less than 3,000 Square Feet in Gross Floor Area)

| Building elements or parts to be examined | Regulations, Code or Guidelines reference |
| --- | --- |
| Building Type by function | DCA Regulations |
| Building Type by fire resistance | Section 3 of Code |
| Roof | Guidelines Section B.5 |
| Cross Sections required | Admin. of the Guidelines |
| Structure | Admin.. of the Guidelines |
| Site layout | Development Standards - Section 19 of Code |
| Site plan | Guidelines Admin. and DCA. Regulations |
| Location | Land use plan |
| Floor - dimensions | Table 5-1 of Code |
| Floor - concrete | Guidelines Section B.4 |
| Floor - timber | Guidelines Section C.3 |
| Lighting and electricity | Guidelines Section G.7 |
| Ventilation | Section 502.6 of Code |
| Sewerage and waste disposal | Section F of Guidelines |
| Water Storage | Section F of Guidelines |
| Plumbing | Section F of Guidelines |
| Parking | Table 19-7 of Section 19 of Code and DCA regulations |
| Access | Section 19 of Code |
| Foundations |  |
| Concrete buildings | Section B of Guidelines |
| Timber buildings | Section C of Guidelines |
| Steel buildings | Section D of Guidelines |
| Fire Resistance Construction | Section E of Guidelines |

APPENDIX 1B

RESULTS OF EXAMINATION OF PLAN SUBMITTED FOR DEVELOPMENT APPROVAL OR FOR A BUILDING PERMIT (The relevant section of the Guidelines to be quoted for all items reviewed)

Building Inspector

Date

Application Number

Date Submitted to the DCA

Type of Development: __________________________________

____________________________________________________

Name of Owner  Person Interviewed (if any)

| Development elements reviewed | Satisfactory | Not satisfactory |
| --- | --- | --- |
|  | Guidelines section | Guidelines section |
| Site Layout |  |  |
| Foundation layout, sizes |  |  |
| Concrete ground floors- Compaction, floor thickness and reinforcement |  |  |
| Concrete suspended floors - thickness and reinforcement |  |  |
| Walls (sizes and reinforcement) |  |  |
| Columns Spacing, sizes and reinforcement |  |  |
| Roof - type and pitch |  |  |
|  | Guidelines Section | Guidelines Section |
| Roof member sizes |  |  |
| Septic tank or Cess pit - location and sizes |  |  |
| Soakaway Pit - location, depth and size |  |  |
| Water cistern - location, type, size, and construction materials used |  |  |
| Concrete water cistern - location, wall thickness, reinforcement |  |  |
| Electricity (with electrical inspector) |  |  |
| Plumbing - pipe sizes and connections |  |  |
| Rain water disposal - size of gutters and location of disposal of rain water |  |  |

APPENDIX 2

REQUEST FOR INSPECTION

(Sample form. Similar forms are to be used for all elements to be inspected)

FORM NO 1:  Request for Inspection of SETTING OUT

To:	 		Development Control Authority

Permission Number:	_______________________________

Type of Development:	_______________________________

_______________________________

_______________________________

Name of Developer:	_______________________________

_______________________________

Date inspection required:	________________________________

Name of Builder:		________________________________

Date of request:		________________________________

Signature of Builder:	________________________________

Proposed date of inspection: _____________________________

Inspection not scheduled: _______________________________

(Reasons)

________________________________

________________________________

Sgd. Building Inspector	_______________________________

Date:			_______________________________

Note: This form is to be used for inspections of all elements as identified in the Code. The builder should ensure that the request reaches the Building Inspector at least 48 hours before the inspection is required.

If the Building Inspector cannot meet the date required the builder must be informed by noting this on the form and signing his name and date. The builder must be aware that the responsibility for conforming to the Code is his/her's, and not the DCA.

APPENDIX 3.

BUILDING INSPECTION REPORT FORM

Name of Inspector: _____________________________________

Date and time of inspection: _____________________________

Certificate Number: __________________________________

Date Approved: _______________________________________

Type of Development: __________________________________

Name of Owner: _____________________________________

Person Interviewed: ____________________________________

| ELEMENTS INSPECTED | SATISFACTORY | NOT SATISFACTORY |
| --- | --- | --- |
|  | Guidelines reference | Guidelines reference |
| Site Layout |  |  |
| Foundation |  |  |
| Floors |  |  |
| Walls |  |  |
| Columns |  |  |
| Belt Beam |  |  |
| Roof |  |  |
| Septic Tank or Cess Pit |  |  |
| Soakaway Pit |  |  |
| Water Cistern |  |  |
| Electricity |  |  |
| Plumbing |  |  |
| Rain water guttering and disposal |  |  |

GENERAL COMMENTS AND RECOMMENDATIONS:

APPENDIX 4.

Monthly Report Form

(Sample headings only)

BUILDINGS UNDER CONSTRUCTION  DURING MONTH OF :

Name of Inspector 					Date

| Permission No | Plot and Parcel No. | Date Approved | Type of Development | Stage Reached | Is Work as Approved | Comments |
| --- | --- | --- | --- | --- | --- | --- |

APPENDIX 5

DESIGN REQUIREMENTS FOR CONSIDERATION BY BUILDING CONSULTANTS

| Item No. | Description | Considered |  |
| --- | --- | --- | --- |
|  |  | Yes | No |
| A - ARCHITECTURAL |  |  |  |
| A-1 | Fire resisting assemblies |  |  |
| A-2 | Fire separations and their continuity |  |  |
| A-3 | Closures, including tightness and operation |  |  |
| A-4 | Egress systems including access to exits within suites and floor areas |  |  |
| A-5 | Performance and safety of guardrails, handrails etc |  |  |
| A-6 | Structural capacity of architectural components including anchorage and restraints |  |  |
| A-7 | Sound control |  |  |
| A-8 | Landscaping design |  |  |
| A-9 | Fire resistance |  |  |
| A-10 | Access requirements for persons with disabilities |  |  |
| A-11 | Review of applicable shop drawings |  |  |
| A-12 | Damp-proofing and waterproofing walls below grade |  |  |
| A-13 | Elevating devices |  |  |
| A-14 | Wall cladding systems |  |  |
| A-15 | Roof systems and cladding |  |  |
| A-16 | Exterior glazing |  |  |
| A-17 | Integration of building requirements |  |  |
| A-18 | Conditions of development permit issued by the Town Planner |  |  |
| A-19 | Conditions of detailed and building permit issued by the Building Authority |  |  |
| B - STRUCTURAL ENGINEERING |  |  |  |
| B-1 | Structural capacity of structural components (all beams, columns, floor and roof systems) of the building including anchorage and seismic restraints |  |  |
| B-2 | Structural aspects of foundations |  |  |
| B-3 | Review of all applicable shop drawings |  |  |
| B-4 | Structural aspects of all precast members including connections and restraint devices |  |  |
| B-5 | Structural aspects of pre and post tensioned design |  |  |
| C - MECHANICAL ENGINEERING |  |  |  |
| C-1 | AC systems and devices |  |  |
| C-2 | Fire dampers at required fire separations |  |  |
| C-3 | Continuity of fire separations at AC penetrations |  |  |
| C-4 | Functional testing of mechanically related fire emergency systems |  |  |
| C-5 | Structural capacity of all mechanical systems including anchorage and seismic restraints |  |  |
| C-6 | Review of all applicable shop drawings |  |  |
| C-7 | Maintenance manuals for AC systems |  |  |
| D - CIVIL ENGINEERING |  |  |  |
| D-1 | Site drainage systems |  |  |
| D-2 | Site grading |  |  |
| D-3 | Embankments and retaining walls |  |  |
| D-4 | Access roads |  |  |
| E - PLUMBING |  |  |  |
| E-1 | Roof drainage systems |  |  |
| E-2 | Continuity of fire separations at plumbing penetrations |  |  |
| E-3 | Functional testing of plumbing related fire emergency systems |  |  |
| E-4 | Review of all applicable shop drawings |  |  |
| E-5 | Water supply for landscaping |  |  |
| E-6 | Structural capacity of plumbing systems including anchorage and restraints |  |  |
| G- LANDSCAPING |  |  |  |
| G-1 | Miscellaneous work. See A-8, D-1, D-2, D-3, E-5, F-5 |  |  |
| G-2 | Soil replacement |  |  |
| G-3 | Planting |  |  |

Certificate of the Prime Consultant

I certify that the building for which an application for a building permit has been requested has been designed in accordance with the requirements of the Building Code. Where there is/are (a) deviation/s from the requirements of the Code such deviations have been noted on the plans and the Code or Standard used has been referenced.

Signed: ----------------------------------------------------------------

Prime Consultant

Date:  ------------------------------------------------------------------

Note: This form must be submitted to the Director in support of an application for a building permit. A building permit will not be issued unless this form has been completed and submitted and approved by the Director.

APPENDIX 6

CERTIFICATE OF PRACTISING STRUCTURAL ENGINEER

1	Background

The accompanying certificate provides information on the technical requirements of the structural design of buildings as required under the provisions of the Code.

This form is to be presented to the Director with the structural plans for the buildings conforming to the categories listed on the form.  Completion of the form will assist the Director in making more appropriate decisions with respect to compliance of the structure with the  standards in the Code.

The use of this form does not increase the work of the structural engineer. On the contrary, it provides a logical framework within which the engineer’s work may be organised.

Note:	The categories of buildings for which this form shall be used include those buildings listed in Groups A, B, C and F in Section 3 of the Code plus hotels of more than 20 rooms and multi-storey condominiums of more than 15 units.

2.	Design

This form is to be used for submissions of applications to the Director for a building permit to construct new buildings, additions to existing buildings and renovations involving changes of use.

Owner's Name:

Building:

Location:

3.	Documents Attached - if and as required by the Director:

3.1	Drawings

-	outline drawings illustrating the overall structural scheme

-	construction details

3.2	Philosophy and concept of structural design and design criteria: (Attach report).

3.3	Safe foundation bearing pressure:  Attach summary geotechnical report.

3.4	Specifications: Attach separate sheets with the technical specifications including materials, workmanship, testing and any special construction sequencing.

3.5	Calculations: Attach separate sheets with calculations for the overall structural frame and for typical details.

3.6 	Building Class:

3.7	Existing Building Age:

4.	Design Criteria

4.1	Gravity Live Loads:

a)	roof

b)	upper floors

c)	ground floor

4.2	Wind Loading:

a)	Basic and Design Wind Velocities:

b)	Terrain Category:

i)	ground roughness

ii)	topography

c).	Building life or safety or importance considerations

d)	Pressure Coefficients:

i).	External roof (max):

ii).	External roof (min):

iii)	External walls (max):

iv)	External walls (min):

v)	Internal (max):

vi).	Internal (min):

4.3	Earthquake loading:

i)	Zone Z factor:

ii)	Importance I factor:

iii)	Structural system K factor:

iv)	Structural stiffness C factor:

v)	Soils S factor:

4.4	Load combinations:

- dead + fluids

- dead + fluids + live + soil + rain

3.	dead + live + rain + wind

4.	dead + live + earthquake

5.	dead + wind + soil

6.	dead + earthquake + soil

5.	Certificate

I/We* certify that:

1	I am a/we are* Practising Structural Engineer(s)* actively involved in the field of structural engineering design.

2	I/We* have carried out/checked* the structural design and calculations for the above building.

3	The structure for the above-mentioned building has been designed in accordance with the principles of structural mechanics and, if constructed reasonably in accordance with the documents listed above, will be capable of sustaining the combinations of loads to which it will be subjected in accordance with the relevant provisions of the Building Code.  The relevant standards, specifications and references relied upon in the design of the building work are as follows:

4.	If the design does not comply with the relevant standards and the Building Code, state in which areas it differs (attach reports if necessary):

5	This Certificate is valid for ten years from date of issue only if the building structure remains as designed.

6	I/We* have/have not* been engaged to carry out the structural supervision of the construction and will/will not issue a Certificate to certify that the constructed works are in accordance with the drawings.

All documents covered by this certificate shall be endorsed and signed by the Practising Structural Engineer.

Name:

Qualifications

Address:

Signature:

Date:

Note: This form was developed with the assistance of Tony Gibbs

PROCEDURES

FOR THE EXAMINATION

OF PLANS

AND

INSPECTION OF

CONSTRUCTION

PROCEDURES

For the

EXAMINATION OF PLANS

and

INSPECTION OF CONSTRUCTION

Prepared by

Alwyn T. Wason  P.Eng

for the

Post Georges Disaster Mitigation Project

# Footnotes

A corporate member of the Institution of Structural Engineers of the UK or legal engineers registration

Delete where not necessary